## Configuration Regs
| Modbus Register Table for Transmitters Configuration (Read / Write) |  |  |  | Name | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | Tx Temp Ext PT1000 (1) Ext Power | Tx Temp Ext PT1000 (2) Ext Power
Table Position | Modbus Registers | Name | Bytes | Description | Enless Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX TEMP CONT1 MP 600-033 | TX TEMP CONT2 MP 600-233
[5 empty] | ENxxx | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311
3 | 45083 | DeviceID( Higher word) | 2 | Device ID HO |  | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID
| 45084 | DeviceID( Lower word) | 2 | Device ID LO |  | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID
| 45085 | Tx Period | 2 | Transmission Period in mins |  | Tx Period (5min) | Tx Period (15min) | Tx Period (15min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min)
| 45086 | TWU Period | 2 | Time windown Upgrade Time in mins |  | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0)
| 45087 | Alarm Threshold Period | 2 | Alarm Threshold Period in Secs (time before alarm is sent) |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45088 | Tx Type | 2 | Transmitter Type |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| 45089 | Alarm Setting | 2 | Alarm Setting |  | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Input Period (Hi) | Temp1 Hi - P1 (0) | Analog Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0)
| 45090 | Alarm Setting | 2 | Alarm Setting |  | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Input Period (Lo) | Temp1 Lo - P2 (0) | Analog Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0)
| 45091 | Alarm Setting | 2 | Alarm Setting |  | Hum Hi - P3 (0) | Hum Hi - P3 (0) | Hum Hi - P3 (0) | zero | Ch1 Flow Time - P3 (0) | Ch1 Flow Time - P3 (0) | Ch1 Flow Time - P3 (0) | Ch2 Input Period (Hi) | Temp2 Hi - P3 (0) | Loop Period - P3 (0) | Hum Hi - P3 (0) | zero | zero | Temp2 Hi - P3 (0)
| 45092 | Alarm Setting | 2 | Alarm Setting |  | Hum Lo - P4 (0) | Hum Lo - P4 (0) | Hum Lo - P4 (0) | zero | Ch1 Leak Threshold - P4 (0) | Ch1 Leak Threshold - P4 (0) | Ch1 Leak Threshold - P4 (0) | Ch2 Input Period (Lo) | Temp2 Lo - P4 (0) | zero | Hum Lo - P4 (0) | zero | zero | Temp2 Lo - P4 (0)
| 45093 | Alarm Setting | 2 | Alarm Setting |  | zero | VOC Hi - P5 (0) | VOC Hi - P5 (0) | zero | Ch2 Flow Hi - P5 (0) | Ch2 Flow Hi - P5 (0) | Ch2 Flow Hi - P5 (0) | zero | zero | zero | zero | zero | zero | zero
| 45094 | Alarm Setting | 2 | Alarm Setting |  | zero | VOC Lo - P6 (0) | VOC Lo - P6 (0) | zero | Ch2 Flow Lo - P6 (0) | Ch2 Flow Lo - P6 (0) | Ch2 Flow Lo - P6 (0) | zero | zero | zero | zero | zero | zero | zero
| 45095 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | CO2 Hi - P7 (0) | zero | Ch2 Flow Time - P7 (0) | Ch2 Flow Time - P7 (0) | Ch2 Flow Time - P7 (0) | zero | zero | zero | zero | zero | zero | zero
| 45096 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | CO2 Lo - P8 (0) | zero | Ch2 Leak Threshold - P8 (0) | Ch2 Leak Threshold - P8 (0) | Ch2 Leak Threshold - P8 (0) | zero | zero | zero | zero | zero | zero | zero
| 45097 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | zero | zero | zero | zero | zero | zero | zero
| 45098 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | zero | zero | zero | zero | zero | zero | zero
| 45099 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | zero | zero | zero | zero | zero | zero | zero
| 45100 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | zero | zero | zero | zero | zero | zero | zero
| 45101 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45102 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45103 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45104 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45105 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45106 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45107 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45108 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45109 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45110 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45111 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45112 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45113 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45114 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45115 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45116 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45117 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45118 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45119 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45120 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45121 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45122 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero